## DC Feeder Mapping
Tagname | Inverter | Submodule | DC Feeder | String Count | PV Module | String Size | POA Group
b0101dc1/current_dc_input_01 | b0101in1 |  | CB 01 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_02 | b0101in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_03 | b0101in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_04 | b0101in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_05 | b0101in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_06 | b0101in1 |  | CB 06 | 18 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_07 | b0101in1 |  | CB 07 | 12 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_08 | b0101in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_09 | b0101in1 |  | CB 09 | 18 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_10 | b0101in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_11 | b0101in1 |  | CB 11 | 21 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_12 | b0101in1 |  | CB 12 | 18 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_13 | b0101in1 |  | CB 13 | 15 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_14 | b0101in1 |  | CB 14 | 12 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_15 | b0101in1 |  | CB 15 | 21 | JKM 395 mono | 26 | A
b0101dc1/current_dc_input_16 | b0101in1 |  | CB 16 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_01 | b0102in1 |  | CB 01 | 18 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_02 | b0102in1 |  | CB 02 | 18 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_03 | b0102in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_04 | b0102in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_05 | b0102in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_06 | b0102in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_07 | b0102in1 |  | CB 07 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_08 | b0102in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_09 | b0102in1 |  | CB 09 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_10 | b0102in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_11 | b0102in1 |  | CB 11 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_12 | b0102in1 |  | CB 12 | 21 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_13 | b0102in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_14 | b0102in1 |  | CB 14 | 24 | JKM 395 mono | 26 | A
b0102dc1/current_dc_input_15 | b0102in1 |  | CB 15 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_01 | b0103in1 |  | CB 01 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_02 | b0103in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_03 | b0103in1 |  | CB 03 | 21 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_04 | b0103in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_05 | b0103in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_06 | b0103in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_07 | b0103in1 |  | CB 07 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_08 | b0103in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_09 | b0103in1 |  | CB 09 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_10 | b0103in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_11 | b0103in1 |  | CB 11 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_12 | b0103in1 |  | CB 12 | 20 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_13 | b0103in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_14 | b0103in1 |  | CB 14 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_15 | b0103in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0103dc1/current_dc_input_16 | b0103in1 |  | CB 16 | 12 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_01 | b0104in1 |  | CB 01 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_02 | b0104in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_03 | b0104in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_04 | b0104in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_05 | b0104in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_06 | b0104in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_07 | b0104in1 |  | CB 07 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_08 | b0104in1 |  | CB 08 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_09 | b0104in1 |  | CB 09 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_10 | b0104in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_11 | b0104in1 |  | CB 11 | 20 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_12 | b0104in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_13 | b0104in1 |  | CB 13 | 18 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_14 | b0104in1 |  | CB 14 | 18 | JKM 395 mono | 26 | A
b0104dc1/current_dc_input_15 | b0104in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_01 | b0105in1 |  | CB 01 | 12 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_02 | b0105in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_03 | b0105in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_04 | b0105in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_05 | b0105in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_06 | b0105in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_07 | b0105in1 |  | CB 07 | 18 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_08 | b0105in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_09 | b0105in1 |  | CB 09 | 12 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_10 | b0105in1 |  | CB 10 | 18 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_11 | b0105in1 |  | CB 11 | 18 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_12 | b0105in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_13 | b0105in1 |  | CB 13 | 20 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_14 | b0105in1 |  | CB 14 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_15 | b0105in1 |  | CB 15 | 24 | JKM 395 mono | 26 | A
b0105dc1/current_dc_input_16 | b0105in1 |  | CB 16 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_01 | b0106in1 |  | CB 01 | 12 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_02 | b0106in1 |  | CB 02 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_03 | b0106in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_04 | b0106in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_05 | b0106in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_06 | b0106in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_07 | b0106in1 |  | CB 07 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_08 | b0106in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_09 | b0106in1 |  | CB 09 | 12 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_10 | b0106in1 |  | CB 10 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_11 | b0106in1 |  | CB 11 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_12 | b0106in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_13 | b0106in1 |  | CB 13 | 20 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_14 | b0106in1 |  | CB 14 | 24 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_15 | b0106in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_16 | b0106in1 |  | CB 16 | 18 | JKM 395 mono | 26 | A
b0106dc1/current_dc_input_17 | b0106in1 |  | CB 17 | 18 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_01 | b0201in1 |  | CB 01 | 18 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_02 | b0201in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_03 | b0201in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_04 | b0201in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_05 | b0201in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_06 | b0201in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_07 | b0201in1 |  | CB 07 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_08 | b0201in1 |  | CB 08 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_09 | b0201in1 |  | CB 09 | 18 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_10 | b0201in1 |  | CB 10 | 18 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_11 | b0201in1 |  | CB 11 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_12 | b0201in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_13 | b0201in1 |  | CB 13 | 22 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_14 | b0201in1 |  | CB 14 | 19 | JKM 395 mono | 26 | A
b0201dc1/current_dc_input_15 | b0201in1 |  | CB 15 | 12 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_01 | b0202in1 |  | CB 01 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_02 | b0202in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_03 | b0202in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_04 | b0202in1 |  | CB 04 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_05 | b0202in1 |  | CB 05 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_06 | b0202in1 |  | CB 06 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_07 | b0202in1 |  | CB 07 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_08 | b0202in1 |  | CB 08 | 21 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_09 | b0202in1 |  | CB 09 | 23 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_10 | b0202in1 |  | CB 10 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_11 | b0202in1 |  | CB 11 | 18 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_12 | b0202in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_13 | b0202in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_14 | b0202in1 |  | CB 14 | 24 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_15 | b0202in1 |  | CB 15 | 20 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_16 | b0202in1 |  | CB 16 | 15 | JKM 395 mono | 26 | A
b0202dc1/current_dc_input_17 | b0202in1 |  | CB 17 | 10 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_01 | b0203in1 |  | CB 01 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_02 | b0203in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_03 | b0203in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_04 | b0203in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_05 | b0203in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_06 | b0203in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_07 | b0203in1 |  | CB 07 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_08 | b0203in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_09 | b0203in1 |  | CB 09 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_10 | b0203in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_11 | b0203in1 |  | CB 11 | 22 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_12 | b0203in1 |  | CB 12 | 22 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_13 | b0203in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_14 | b0203in1 |  | CB 14 | 18 | JKM 395 mono | 26 | A
b0203dc1/current_dc_input_15 | b0203in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_01 | b0204in1 |  | CB 01 | 18 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_02 | b0204in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_03 | b0204in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_04 | b0204in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_05 | b0204in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_06 | b0204in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_07 | b0204in1 |  | CB 07 | 18 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_08 | b0204in1 |  | CB 08 | 12 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_09 | b0204in1 |  | CB 09 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_10 | b0204in1 |  | CB 10 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_11 | b0204in1 |  | CB 11 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_12 | b0204in1 |  | CB 12 | 20 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_13 | b0204in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_14 | b0204in1 |  | CB 14 | 24 | JKM 395 mono | 26 | A
b0204dc1/current_dc_input_15 | b0204in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_01 | b0205in1 |  | CB 01 | 12 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_02 | b0205in1 |  | CB 02 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_03 | b0205in1 |  | CB 03 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_04 | b0205in1 |  | CB 04 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_05 | b0205in1 |  | CB 05 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_06 | b0205in1 |  | CB 06 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_07 | b0205in1 |  | CB 07 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_08 | b0205in1 |  | CB 08 | 18 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_09 | b0205in1 |  | CB 09 | 18 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_10 | b0205in1 |  | CB 10 | 12 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_11 | b0205in1 |  | CB 11 | 18 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_12 | b0205in1 |  | CB 12 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_13 | b0205in1 |  | CB 13 | 24 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_14 | b0205in1 |  | CB 14 | 20 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_15 | b0205in1 |  | CB 15 | 18 | JKM 395 mono | 26 | A
b0205dc1/current_dc_input_16 | b0205in1 |  | CB 16 | 18 | JKM 395 mono | 26 | A
b0206dc1/current_dc_input_01 | b0206in1 |  | CB 01 | 18 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_02 | b0206in1 |  | CB 02 | 24 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_03 | b0206in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_04 | b0206in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_05 | b0206in1 |  | CB 05 | 23 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_06 | b0206in1 |  | CB 06 | 20 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_07 | b0206in1 |  | CB 07 | 20 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_08 | b0206in1 |  | CB 08 | 23 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_09 | b0206in1 |  | CB 09 | 18 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_10 | b0206in1 |  | CB 10 | 12 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_11 | b0206in1 |  | CB 11 | 18 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_12 | b0206in1 |  | CB 12 | 8 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_13 | b0206in1 |  | CB 13 | 20 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_14 | b0206in1 |  | CB 14 | 24 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_15 | b0206in1 |  | CB 15 | 24 | JKM 400 mono | 26 | A
b0206dc1/current_dc_input_16 | b0206in1 |  | CB 16 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_01 | b0301in1 |  | CB 01 | 18 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_02 | b0301in1 |  | CB 02 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_03 | b0301in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_04 | b0301in1 |  | CB 04 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_05 | b0301in1 |  | CB 05 | 15 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_06 | b0301in1 |  | CB 06 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_07 | b0301in1 |  | CB 07 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_08 | b0301in1 |  | CB 08 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_09 | b0301in1 |  | CB 09 | 15 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_10 | b0301in1 |  | CB 10 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_11 | b0301in1 |  | CB 11 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_12 | b0301in1 |  | CB 12 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_13 | b0301in1 |  | CB 13 | 24 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_14 | b0301in1 |  | CB 14 | 16 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_15 | b0301in1 |  | CB 15 | 20 | JKM 400 mono | 26 | A
b0301dc1/current_dc_input_16 | b0301in1 |  | CB 16 | 18 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_01 | b0302in1 |  | CB 01 | 18 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_02 | b0302in1 |  | CB 02 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_03 | b0302in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_04 | b0302in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_05 | b0302in1 |  | CB 05 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_06 | b0302in1 |  | CB 06 | 12 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_07 | b0302in1 |  | CB 07 | 18 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_08 | b0302in1 |  | CB 08 | 12 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_09 | b0302in1 |  | CB 09 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_10 | b0302in1 |  | CB 10 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_11 | b0302in1 |  | CB 11 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_12 | b0302in1 |  | CB 12 | 20 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_13 | b0302in1 |  | CB 13 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_14 | b0302in1 |  | CB 14 | 24 | JKM 400 mono | 26 | A
b0302dc1/current_dc_input_15 | b0302in1 |  | CB 15 | 18 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_01 | b0303in1 |  | CB 01 | 18 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_02 | b0303in1 |  | CB 02 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_03 | b0303in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_04 | b0303in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_05 | b0303in1 |  | CB 05 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_06 | b0303in1 |  | CB 06 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_07 | b0303in1 |  | CB 07 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_08 | b0303in1 |  | CB 08 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_09 | b0303in1 |  | CB 09 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_10 | b0303in1 |  | CB 10 | 12 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_11 | b0303in1 |  | CB 11 | 18 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_12 | b0303in1 |  | CB 12 | 18 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_13 | b0303in1 |  | CB 13 | 20 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_14 | b0303in1 |  | CB 14 | 24 | JKM 400 mono | 26 | A
b0303dc1/current_dc_input_15 | b0303in1 |  | CB 15 | 21 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_01 | b0304in1 |  | CB 01 | 12 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_02 | b0304in1 |  | CB 02 | 18 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_03 | b0304in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_04 | b0304in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_05 | b0304in1 |  | CB 05 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_06 | b0304in1 |  | CB 06 | 12 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_07 | b0304in1 |  | CB 07 | 12 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_08 | b0304in1 |  | CB 08 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_09 | b0304in1 |  | CB 09 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_10 | b0304in1 |  | CB 10 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_11 | b0304in1 |  | CB 11 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_12 | b0304in1 |  | CB 12 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_13 | b0304in1 |  | CB 13 | 24 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_14 | b0304in1 |  | CB 14 | 20 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_15 | b0304in1 |  | CB 15 | 18 | JKM 400 mono | 26 | A
b0304dc1/current_dc_input_16 | b0304in1 |  | CB 16 | 12 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_01 | b0305in1 |  | CB 01 | 18 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_02 | b0305in1 |  | CB 02 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_03 | b0305in1 |  | CB 03 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_04 | b0305in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_05 | b0305in1 |  | CB 05 | 21 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_06 | b0305in1 |  | CB 06 | 18 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_07 | b0305in1 |  | CB 07 | 12 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_08 | b0305in1 |  | CB 08 | 18 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_09 | b0305in1 |  | CB 09 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_10 | b0305in1 |  | CB 10 | 20 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_11 | b0305in1 |  | CB 11 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_12 | b0305in1 |  | CB 12 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_13 | b0305in1 |  | CB 13 | 24 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_14 | b0305in1 |  | CB 14 | 16 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_15 | b0305in1 |  | CB 15 | 18 | JKM 400 mono | 26 | A
b0305dc1/current_dc_input_16 | b0305in1 |  | CB 16 | 14 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_01 | b0306in1 |  | CB 01 | 12 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_02 | b0306in1 |  | CB 02 | 12 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_03 | b0306in1 |  | CB 03 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_04 | b0306in1 |  | CB 04 | 24 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_05 | b0306in1 |  | CB 05 | 24 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_06 | b0306in1 |  | CB 06 | 24 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_07 | b0306in1 |  | CB 07 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_08 | b0306in1 |  | CB 08 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_09 | b0306in1 |  | CB 09 | 12 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_10 | b0306in1 |  | CB 10 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_11 | b0306in1 |  | CB 11 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_12 | b0306in1 |  | CB 12 | 20 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_13 | b0306in1 |  | CB 13 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_14 | b0306in1 |  | CB 14 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_15 | b0306in1 |  | CB 15 | 18 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_16 | b0306in1 |  | CB 16 | 22 | JKM 400 mono | 26 | A
b0306dc1/current_dc_input_17 | b0306in1 |  | CB 17 | 22 | JKM 400 mono | 26 | A
Note on A1: Cayt Schlichting: Insert DC Feeder tags here. Standard naming: b0101dc1/current_dc_input_01 Fully Modular (TMEIC) Naming: b0101dc1/dc2_current_dc_input_01 - Capitalization doesn't matter - Feeder number at the end of the tag needs to be padded. EX: 2 is "_02"
Note on B1: Cayt Schlichting: This should be Inverter (or Skid) identifier - not just the block number - and should match the Inverter number on the Inverter Mapping sheet. Example: b0101in1 or b0203in2 If you already have the Tagname column populated, you can use this formula to pull the inverter name out. =REPLACE(LEFT(A2,8),6,2,"IN") However, if block number is provided, it is assumed to be inverter 1 on that block. EX: b0202 becomes b0202in1
Note on C1: Cayt Schlichting: Only enter the Submodule name if it is a fully modular inverter (like TMEICs) or string inverters. Submodule naming convention: b0103in1/in02 If you already have the Tagname column populated, you can use this formula to pull the submodule name out. =CONCAT(REPLACE(LEFT(A2,8),6,2,"IN"),"/IN",TEXT(TEXTBEFORE(TEXTAFTER(LOWER(A2),"/dc"),"_cur"),"00"))
Note on D1: Cayt Schlichting: Preferred format of "CB 01" . DC Feeder # should be padded to two digits.
Note on E1: Cayt Schlichting: The number of strings going into a DC Feeder.
Note on F1: Cayt Schlichting: The PV Modules in this column must exactly match a Module listed on the PV Modules sheet. This is case sensitive. Preferred format: <manufacturer> <Wattage> <bi/mono> EX: First Solar 460 mono IF String Size is appended to some modules, I recommend removing that from the module name.
Note on G1: Cayt Schlichting: The number of PV modules on a string.
Note on H1: Cayt Schlichting: 99% of the time, this should be left blank. POA Group association with DC Feeders happens on the backend based off the information in the POA Groups Table

## PV Modules
Module | Manufacturer | Length | Bifacial Factor | Pmax | Imp | Vmp | Tk_Pmp | Tk_Vmp | Tk_Imp
JKM 395 mono | Jinko | 2.008 | 0 | 395 | 9.55 | 41.4 | -0.0036 | -0.0028 | 0.00048
JKM 400 mono | Jinko | 2.008 | 0 | 400 | 9.6 | 41.7 | -0.0036 | -0.0028 | 0.00048
Note on A1: Cayt Schlichting: Entries must exactly match what is on the DC Feeder mapping page. I recommend copying the values form that sheet. Preferred format: <manufacturer> <Wattage> <bi/mono>
Note on C1: Cayt Schlichting: In Meters. This should be the total length of the module(s) upon installation. For a single module installed in Portrait (vertically), this is the length of the module. However if you have modules installed horizontally, then it would be module width X # of modules + gap space. You may be given a GCR and row spacing and can also calculate the length from that. Provide all decimal points found on spec sheet.
Note on D1: Cayt Schlichting: Bifacial Factor for the PV Module. If Monofacial, enter 0. Enter as the integer percent. EX: 75% Bifacial Factor should be entered as 75
Note on E1: Cayt Schlichting: In Watts
Note on F1: Cayt Schlichting: In Amps
Note on G1: Cayt Schlichting: In Volts
Note on H1: Cayt Schlichting: Pmp Temperature coefficient should be negative. Enter as a decimal. EX: -.28% should be -.0028
Note on I1: Cayt Schlichting: Vmp Temperature coefficient should be negative. Enter as a decimal. EX: -.28% should be -.0028
Note on J1: Cayt Schlichting: Enter as a decimal. EX: .04% should be .0004

## Inverter Mapping
Inverter | AC Apparent Capacity (KVA) | AC Capacity (KW) | DC/AC Corr Factor | AC Voltage | Pos Tolerance | Neg Tolerance | PPA | DC Capacity | Row Spacing | Tracker Type | Axis Tilt | Axis Azimuth | Cross axis tilt | Max Angle | Backtrack | Fixed | Num Submodules | Min. Operating Ambient Temp. (°C) | Max. Operating Ambient Temp. (°C) | Temp. Derate Threshold 1 - Start (°C) | Temp. Derate Threshold 1 - Start (kW) | Temp. Derate Threshold 1 - End (°C) | Temp. Derate Threshold 1 - End (kW) | Temp. Derate Threshold 2 - Start (°C) | Temp. Derate Threshold 2 - Start (kW) | Temp. Derate Threshold 2 - End (°C) | Temp. Derate Threshold 2 - End (kW)
b0101in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3296.67 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6 |  |  |  | 2700
b0102in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3481.53 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0103in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3378.83 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0104in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3471.26 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0105in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3409.64 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0106in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3409.64 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0201in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3317.21 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0202in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3449.03 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0203in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3471.26 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0204in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3348.02 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0205in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3348.02 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0206in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3328 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0301in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3390.4 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0302in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3265.6 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0303in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3359.2 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0304in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3328 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0305in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3359.2 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
b0306in1 | 3465 | 2700 | 0.985 |  |  |  |  | 3286.4 | 6.4008 | NXT | 0 | 180 | 0 | 60 | TRUE |  | 6
Note on A1: Cayt Schlichting: This must match the inverter identifier on the DC Feeder Mapping page. It's easiest to copy all the inverters from DC Mapping, then use the "Remove Duplicates" functionality in Excel (Found on the Data tab).
Note on D1: Cayt Schlichting: Enter as a decimal EX: Enter .985 to represent 98.5%
Note on E1: Cayt Schlichting: In Volts. Used for creating voltage bands in the Inverter Phase Voltage plots.
Note on F1: Cayt Schlichting: The inverter's positive tolerance percentage for AC Voltage. EX: Enter 5 for +5%
Note on G1: Cayt Schlichting: The inverter's negative tolerance percentage for AC Voltage. EX: Enter 10 for -10% This can technically be entered as positive or negative, the code will force it to negative
Note on H1: Cayt Schlichting: If Multiple PPAs, you can specify the PPAs here. If left blank, PPA will be labeled "und" for undefined.
Note on I1: Cayt Schlichting: This should come from the engineering drawing, you should not calculate it manually from DC Feeder mapping
Note on J1: Cayt Schlichting: In Meters
Note on K1: Cayt Schlichting: Add the Type of Tracking system here. EX: ATI, NXT, or similar. If left blank, tracker type will be labeled "und" for undefined.
Note on L1: Cayt Schlichting: Generally 0. The tilt, or slope, along the tracker tube. This number must always be positive. The direction of the slope is determined by the Azimuth. A tilt of 1 degree, with an azimuth of 180 indicates the array faces slightly South. For a North-facing tilt on the tracker tube, you must enter a positive tilt value, then use an Azimuth of 0. For FIXED systems, this is the Surface Tilt of the system
Note on M1: Cayt Schlichting: Angle (clockwise from North) of the Tracker Tube (0-360), where the angle points downhill. Generally tracker tubes run N/S, and we use "180". Note that either 0 or 180 can be used for a N/S tube on flat land. 180 is used because the site is assumed to slope South (if at all). For FIXED systems, this is the azimuth angle of the modules surface. A South facing fixed mount system will be 180.
Note on N1: Cayt Schlichting: Generally 0. This would be the degrees of the East/West slope. This can be positive or negative (determined by the right hand rule w/ the thumb pointing along the Azimuth). In other words, Positive would be in the direction 90 degrees clockwise from your azimuth. Negative would be in the direction 90 degrees counter-clockwise from your azimuth. (Technically) cross-axis tilt is the slope that is perpendicular to the tracker tube. Example: If you have a site that has a 2 degree slope facing slightly East (and no North/South component to the slope), then you can configure that two ways: Tilt: 0 Azimuth: 180 Cross-axis Tilt: -2 OR Tilt: 0 Azimuth: 0 Cross-axis Tilt: 2 For FIXED arrays, enter 0.
Note on O1: Cayt Schlichting: The maximum angle the tracker tube can rotate the module. For FIXED arrays enter 0.
Note on P1: Cayt Schlichting Enter True if the tracker is backtracking, False if it is not backtracking. This setting is ignored if Fixed is set to True.
Note on Q1: Cayt Schlichting: Defaults to False (if left blank)
Note on U1: Cayt Schlichting: The temperature at which the AC Capacity is provided.
Note on V1: Cayt Schlichting: SAME AS AC Capacity
Note on W1: Cayt Schlichting: The temperature at the end of the first derate range. This may be in the form of the temperature at which the second AC Capacity is given.
Note on X1: Cayt Schlichting: The AC Capacity at the end of the first derate range. This may be in the form of a second AC Capacity at a certain temperature.
Note on Y1: Cayt Schlichting: SAME AS Temp Derate Threshold 1 End (if there is a second range)
Note on Z1: Cayt Schlichting: SAME AS Temp Derate Threshold 1 End (if there is a second range)
Note on AA1: Cayt Schlichting: The temperature at the end of the second derate range. Blank if no second derate range.
Note on AB1: Cayt Schlichting: The AC Capacity at the end of the second derate range. Blank if no second derate range.

## MET Mapping
MET Block | POA Group | POA Option | Notes
B0103 | A | Pyranometer
B0206 | A | Pyranometer
B0305 | A | Pyranometer
Note on A1: Cayt Schlichting: Block number (EX: b0203) that contains a MET station or POA sensor of some kind. [Rare] If there are multiple stations per block and you only want to use one of them, you can specify the station number (EX: b0203ws1 if there is also a b0203ws2). Note: If there is an "is1" and "ws1" on a block, you don't need to specify the station - just enter the block number. Your POA Option will determine what type of sensors to use (ex: refmod vs pyranometers)
Note on B1: Cayt Schlichting: AFTER PRE RUN: Copy over the auto-generated groups for each MET from the pre-run output file. If there is >1 Group listed, you need to chose only 1. See "Running the Tool" in SharePoint for more details. Each unique group listed on the "POA Groups" tab should be assigned to at least one MET Block on this tab.
Note on C1: Cayt Schlichting: AFTER PRE RUN: Select a POA Option from the dropdown. This should be the primary sensor for the capacity test.
Note on D1: Cayt Schlichting: Optional spot to include notes on each weather station. EX: you may find it useful to put what types of sensors are on each station (refmod, pyranometer, etc)

## POA Groups
AFTER PRE RUN: Paste the entire POA Group Combos table (with headers) from the "POA Groupings" file below.
| POA Group | Group Name | ppa | pv_id | gcr | bf | tracker | axis_tilt | axis_azimuth | cross_axis_tilt | max_angle | backtrack | fixed | row_spacing | manu | pmax | length | imp | vmp | tk_pmp | tk_vmp | tk_imp
0 | A | und | und | jkm 395 mono | 0.31371 | 0 | nxt | 0 | 180 | 0 | 60 | TRUE | FALSE | 6.4008 | jinko | 395 | 2.008 | 9.55 | 41.4 | -0.0036 | -0.0028 | 0.00048
173 | A | und | und | jkm 400 mono | 0.31371 | 0 | nxt | 0 | 180 | 0 | 60 | TRUE | FALSE | 6.4008 | jinko | 400 | 2.008 | 9.6 | 41.7 | -0.0036 | -0.0028 | 0.00048

## Clearsky Groups
[RARE] AFTER PRE RUN: ONLY use if overriding the Clearsky Group (Modeled POS) for a controler unit.